## READ ME
Ibri sewer — load calculation, step by step
Every value is calculated live from the 'Inputs' sheet. Change an input (e.g. occupancy 6.0 -> 4.9) and the whole workbook follows.
Sheets:
Inputs all criteria values with their PAM-GUD-201 page refs. Yellow cells are editable.
Population the 25 project towns, NCSI series at the model years. Source and method explained on the sheet.
Load water demand -> wastewater -> infiltration -> Qadf -> peak factor -> peak flow, one row per model year.
By Town 2055 the same load split per town. Non-domestic + governmental volume is placed on non-residential
plot area, not spread per person (GUD-201 §7.3.2-7.3.3 — see A7 note).
Saturation how much population the plots can hold at a given occupancy, and when the projection hits it.
Colour code: yellow fill = input, edit these ¦ green text = pulled from another sheet ¦ black = formula or data.
Three cautions:
1. Occupancy 6.0 and 1 dwelling/plot are unconfirmed [GAP-5]. Measured anchor: ~7.0 persons per built plot.
2. The 22% / 14% ratios are the GUD-201 fallback, not the method. Table 12 (floor areas, beds, pupils) replaces them when data arrives.
3. The NCSI projection never levels off (691k by 2100). The 'ultimate' case must come from land capacity — see Saturation.

## Inputs
Inputs — every number the calculation uses
Yellow cells are the ones to edit. Nothing else in the workbook is typed in twice.
Parameter | Value | Unit | Source | Status
Domestic consumption (Adh Dhahirah) | 164 | l/c/d | GUD-201 Tab 11, G1-p60 | Standard
Non-domestic ratio | 22% | of domestic | GUD-201 Tab 11, G1-p60 | FALLBACK — Table 12 land-use rates replace this when floor areas / counts arrive
Governmental ratio | 14% | of domestic | GUD-201 Tab 11, G1-p60 | FALLBACK — same as above
Return rate, domestic | 0.85 | - | GUD-201 Tab 19, G1-p71 | Standard
Return rate, non-dom + gov | 0.54 | - | GUD-201 Tab 19, G1-p71 | Standard
Infiltration, new networks | 720 | L/d per km | GUD-201 G1-p72 | CONFLICT — R0 workbook uses 10% of flow; needs an NWS ruling
Peak factor cap | 5 | - | GUD-201 G1-p72 | Standard
STP design margin | 10% | on Qadf | GUD-201 G1-p73 | Standard
Sewer network length | 194 | km | W2 trunk total | PROVISIONAL — laterals not included; effect is small (~140 m3/d)
Occupancy rate | 6 | persons/dwelling | [GAP-5] | UNCONFIRMED — colleague suggests 4.9; get officially from NCSI. See Saturation sheet
Dwellings per plot | 1 | dwellings/plot | [GAP-5] | UNCONFIRMED — pairs with occupancy: measured product is ~7 persons per built plot
Population-basis plots | 46633 | plots | W3 A1 (cadastre) | Grows if MoHUP subdivides or releases land

## Population
Population — the 25 project towns
Source: NCSI wilayat forecast, split to settlements by their frozen census share ('Ibri Sewer Demand R0 2026 08 03.xlsx').
NCSI tracks 239 settlements in Ibri wilayat; the 25 inside the project boundary are these towns (63% of the wilayat).
Every town grows at the same wilayat rate (x1.77-1.79 over 2025-2050) — there is no town-specific growth in the data.
Town | Code | 2025 | 2030 | 2040 | 2050 | 2055 | 2060 | 2100
AD DARIZ | 100110153 | 12134 | 13791 | 17670 | 21638 | 24206 | 27240 | 70340
AD DIBAYSHI | 100130080 | 2469 | 2806 | 3595 | 4402 | 4925 | 5542 | 14311
AL AKHEEDAR | 100140030 | 203 | 230 | 295 | 361 | 404 | 455 | 1174
AL ARAQI | 100110081 | 10952 | 12448 | 15949 | 19530 | 21849 | 24587 | 63490
AL AYNAYN | 100110100 | 4663 | 5300 | 6791 | 8316 | 9303 | 10469 | 27033
AL GHUBAYRAH | 100110254 | 647 | 735 | 942 | 1153 | 1290 | 1452 | 3748
AL JAHLI | 100140081 | 425 | 483 | 618 | 757 | 847 | 953 | 2461
AL JIBAYYAH | 100120081 | 2750 | 3126 | 4005 | 4904 | 5486 | 6174 | 15942
AL MAKHTIBYAH | 100130130 | 125 | 142 | 182 | 223 | 249 | 280 | 724
AL QALI | 100140051 | 195 | 222 | 285 | 348 | 390 | 439 | 1133
AL QURAYN | 100110030 | 562 | 638 | 818 | 1002 | 1121 | 1261 | 3256
AL WAHRAH | 100110231 | 3431 | 3900 | 4997 | 6119 | 6845 | 7703 | 19892
ASH SHIAB | 100110180 | 48 | 55 | 70 | 86 | 96 | 108 | 279
AT TAYYIB | 100120060 | 3428 | 3897 | 4993 | 6114 | 6839 | 7696 | 19874
BAT | 100110255 | 2618 | 2976 | 3813 | 4669 | 5223 | 5877 | 15177
HIJAR | 100140052 | 1058 | 1202 | 1541 | 1886 | 2110 | 2375 | 6132
IBRI | 100100000 | 68713 | 78099 | 100066 | 122535 | 137081 | 154261 | 398339
MIAYRID | 100110082 | 35 | 40 | 51 | 62 | 69 | 78 | 202
SATWAH | 100110151 | 269 | 306 | 392 | 480 | 537 | 604 | 1560
SAYH AL MASARRAT | 100140200 | 477 | 542 | 694 | 850 | 951 | 1070 | 2764
SHALASHIL | 100120082 | 133 | 151 | 194 | 237 | 265 | 299 | 771
SUWAYDA AL MA | 100120151 | 1596 | 1814 | 2324 | 2846 | 3184 | 3583 | 9252
TANAM | 100130100 | 2167 | 2463 | 3156 | 3864 | 4323 | 4865 | 12562
USAYBUQ | 100140082 | 93 | 106 | 136 | 166 | 186 | 209 | 540
WADI AL MANKAS | 100110070 | 53 | 60 | 77 | 95 | 106 | 119 | 308
TOTAL |  | 119244 | 135532 | 173654 | 212643 | 237885 | 267699 | 691264

## Load
Load — from population to peak flow, one row per model year
Chain per GUD-201 §7 (G1-p58..73): domestic water -> non-dom + gov -> return rates -> infiltration -> Qadf -> Peltier peak factor -> peak flow -> +10% STP margin.
Year | Population | Domestic water m³/d | Non-domestic m³/d | Governmental m³/d | Total water m³/d | WW domestic m³/d | WW non-dom+gov m³/d | Infiltration m³/d | Qadf m³/d | Qm L/s | Peak factor | Peak flow m³/d | STP design m³/d (+margin)
2025 | 119244 | 19556.016 | 4302.3235 | 2737.8422 | 26596.1818 | 16622.6136 | 3801.6895 | 139.68 | 20563.9831 | 238.0091 | 1.5648 | 32178.9143 | 22620.3814
2030 | 135532 | 22227.248 | 4889.9946 | 3111.8147 | 30229.0573 | 18893.1608 | 4320.977 | 139.68 | 23353.8178 | 270.2988 | 1.5608 | 36451.209 | 25689.1996
2040 | 173654 | 28479.256 | 6265.4363 | 3987.0958 | 38731.7882 | 24207.3676 | 5536.3674 | 139.68 | 29883.415 | 345.8729 | 1.5538 | 46431.96 | 32871.7565
2050 | 212643 | 34873.452 | 7672.1594 | 4882.2833 | 47427.8947 | 29642.4342 | 6779.3991 | 139.68 | 36561.5133 | 423.1657 | 1.5486 | 56619.6035 | 40217.6646
2055 | 237885 | 39013.14 | 8582.8908 | 5461.8396 | 53057.8704 | 33161.169 | 7584.1544 | 139.68 | 40885.0034 | 473.2061 | 1.546 | 63206.9902 | 44973.5038
2060 | 267699 | 43902.636 | 9658.5799 | 6146.369 | 59707.585 | 37317.2406 | 8534.6724 | 139.68 | 45991.593 | 532.3101 | 1.5433 | 70980.7971 | 50590.7523
2100 | 691264 | 113367.296 | 24940.8051 | 15871.4214 | 154179.5226 | 96362.2016 | 22038.6023 | 139.68 | 118540.4839 | 1371.9963 | 1.527 | 181011.0224 | 130394.5323
Note: Qadf here excludes tanker deliveries (~17% of STP inflow, G1-p73) — they go to the STP directly, not through the network.

## By Town 2055
Load by town at 2055 — the pivotal model year
Domestic load follows each town's population. The non-domestic + governmental volume is NOT spread per person:
it is placed on each town's non-residential plot area (commercial, governmental, mosque, industrial — from MoH_Plots).
That is what GUD-201 §7.3.2-7.3.3 intend, and it moves load between towns without changing the total (see A7 note).
Town | Population 2055 | Domestic water m³/d | Non-res plot area m² | Share of non-res area | ND+Gov allocated m³/d | Qadf m³/d (excl. infil.) | Peak factor | Peak flow m³/d
AD DARIZ | 24206 | 3969.784 | 927258 | 10.11% | 1419.7192 | 4140.9648 | 1.6444 | 6809.5938
AD DIBAYSHI | 4925 | 807.7 | 423182 | 4.613% | 647.9314 | 1036.428 | 1.7887 | 1853.8866
AL AKHEEDAR | 404 | 66.256 | 5390 | 0.05876% | 8.2526 | 60.774 | 2.6923 | 163.6239
AL ARAQI | 21849 | 3583.236 | 570099 | 6.215% | 872.8752 | 3517.1032 | 1.6567 | 5826.9059
AL AYNAYN | 9303 | 1525.692 | 624323 | 6.806% | 955.8972 | 1813.0227 | 1.7183 | 3115.3183
AL GHUBAYRAH | 1290 | 211.56 | 116015 | 1.265% | 177.6299 | 275.7461 | 2.0598 | 567.971
AL JAHLI | 847 | 138.908 | 172533 | 1.881% | 264.1643 | 260.7205 | 2.0757 | 541.1682
AL JIBAYYAH | 5486 | 899.704 | 129450 | 1.411% | 198.2001 | 871.7765 | 1.8148 | 1582.1123
AL MAKHTIBYAH | 249 | 40.836 | 6060 | 0.06606% | 9.2784 | 39.721 | 2.9748 | 118.1638
AL QALI | 390 | 63.96 | 149443 | 1.629% | 228.8113 | 177.9241 | 2.1969 | 390.8726
AL QURAYN | 1121 | 183.844 | 67877 | 0.74% | 103.9261 | 212.3875 | 2.1378 | 454.0444
AL WAHRAH | 6845 | 1122.58 | 149424 | 1.629% | 228.7822 | 1077.7354 | 1.7831 | 1921.7528
ASH SHIAB | 96 | 15.744 | 0 | 0% | 0 | 13.3824 | 4.0409 | 54.0771
AT TAYYIB | 6839 | 1121.596 | 2184538 | 23.81% | 3344.7332 | 2759.5125 | 1.6769 | 4627.5534
BAT | 5223 | 856.572 | 127797 | 1.393% | 195.6692 | 833.7476 | 1.8219 | 1519.0162
HIJAR | 2110 | 346.04 | 55173 | 0.6015% | 84.4751 | 339.7505 | 2.0043 | 680.9572
IBRI | 137081 | 22481.284 | 1494055 | 16.29% | 2287.5387 | 20344.3623 | 1.5652 | 31842.3462
MIAYRID | 69 | 11.316 | 252420 | 2.752% | 386.4788 | 218.3171 | 2.1291 | 464.8169
SATWAH | 537 | 88.068 | 2333 | 0.02543% | 3.572 | 76.7867 | 2.5608 | 196.6317
SAYH AL MASARRAT | 951 | 155.964 | 1419623 | 15.48% | 2173.5763 | 1306.3006 | 1.7572 | 2295.4039
SHALASHIL | 265 | 43.46 | 396 | 0.004317% | 0.60631 | 37.2684 | 3.0226 | 112.6476
SUWAYDA AL MA | 3184 | 522.176 | 70284 | 0.7662% | 107.6114 | 501.9598 | 1.9149 | 961.1927
TANAM | 4323 | 708.972 | 36661 | 0.3997% | 56.1314 | 632.9372 | 1.8695 | 1183.2557
USAYBUQ | 186 | 30.504 | 503 | 0.005483% | 0.77014 | 26.3443 | 3.311 | 87.2254
WADI AL MANKAS | 106 | 17.384 | 188166 | 2.051% | 288.0998 | 170.3503 | 2.2122 | 376.8443
TOTAL | 237885 | 39013.14 | 9173003 |  | 14044.7304 | 40745.3234 |  | 67747.3817
Non-res area source: MoH_Plots class v4 within town boundaries (W3 A7). AT TAYYIB's 218 ha is mostly the industrial estate — Table 12 data will re-price it properly. Peak factors apply at each town's own outlet.

## Saturation
Saturation — how many people the plots can hold, and when we get there
Ceiling = population-basis plots x dwellings per plot x occupancy rate.
The projection (right-hand table) keeps growing at ~2.3%/yr and never levels off — so the ceiling, not the
projection, defines 'ultimate'. Measured today: ~7.0 persons per built plot (NCSI 2025 pop ÷ built plots).
If occupancy is really 4.9, dwellings per plot must be ~1.2-1.4 for the sums to match the census.
Occupancy rate | Ceiling population | Year the projection reaches it | Ultimate Qadf m³/d | STP design m³/d (+margin) | Year | Projection total
4.9 | 228501.7 | 2054 | 39277.8168 | 43205.5985 | 2023 | 113224
5.5 | 256481.5 | 2059 | 44070.2417 | 48477.2659 | 2024 | 116456
6 | 279798 | 2062 | 48063.9291 | 52870.322 | 2025 | 119244
[5 empty] | 2026 | 122510
W2 used OR 6.0 -> ultimate Qadf ~49,700 m³/d. At 4.9 the land fills by ~2054 — inside the design horizon, which turns 2055 into a saturation case. |  |  |  |  | 2027 | 125831
[5 empty] | 2028 | 129205
[5 empty] | 2029 | 132629
[5 empty] | 2030 | 135532
[5 empty] | 2031 | 139053
[5 empty] | 2032 | 142639
[5 empty] | 2033 | 144473
[5 empty] | 2034 | 150057
[5 empty] | 2035 | 153183
[5 empty] | 2036 | 157141
[5 empty] | 2037 | 161255
[5 empty] | 2038 | 165514
[5 empty] | 2039 | 169958
[5 empty] | 2040 | 173654
[5 empty] | 2041 | 176964
[5 empty] | 2042 | 180426
[5 empty] | 2043 | 184002
[5 empty] | 2044 | 187687
[5 empty] | 2045 | 191496
[5 empty] | 2046 | 195437
[5 empty] | 2047 | 199510
[5 empty] | 2048 | 203734
[5 empty] | 2049 | 208107
[5 empty] | 2050 | 212643
[5 empty] | 2051 | 217340
[5 empty] | 2052 | 222207
[5 empty] | 2053 | 227248
[5 empty] | 2054 | 232472
[5 empty] | 2055 | 237885
[5 empty] | 2056 | 243497
[5 empty] | 2057 | 249315
[5 empty] | 2058 | 255297
[5 empty] | 2059 | 261424
[5 empty] | 2060 | 267699
[5 empty] | 2061 | 274124
[5 empty] | 2062 | 280700
[5 empty] | 2063 | 287438
[5 empty] | 2064 | 294336
[5 empty] | 2065 | 301399
[5 empty] | 2066 | 308634
[5 empty] | 2067 | 316044
[5 empty] | 2068 | 323628
[5 empty] | 2069 | 331397
[5 empty] | 2070 | 339346
[5 empty] | 2071 | 347492
[5 empty] | 2072 | 355831
[5 empty] | 2073 | 364370
[5 empty] | 2074 | 373116
[5 empty] | 2075 | 382072
[5 empty] | 2076 | 391243
[5 empty] | 2077 | 400630
[5 empty] | 2078 | 410245
[5 empty] | 2079 | 420094
[5 empty] | 2080 | 430177
[5 empty] | 2081 | 440499
[5 empty] | 2082 | 451071
[5 empty] | 2083 | 461898
[5 empty] | 2084 | 472983
[5 empty] | 2085 | 484333
[5 empty] | 2086 | 495957
[5 empty] | 2087 | 507861
[5 empty] | 2088 | 520049
[5 empty] | 2089 | 532531
[5 empty] | 2090 | 545311
[5 empty] | 2091 | 558399
[5 empty] | 2092 | 571801
[5 empty] | 2093 | 585523
[5 empty] | 2094 | 599577
[5 empty] | 2095 | 613966
[5 empty] | 2096 | 628702
[5 empty] | 2097 | 643789
[5 empty] | 2098 | 659242
[5 empty] | 2099 | 675061
[5 empty] | 2100 | 691264