## Flow m3d
Own average dry-weather flow of the 24 subnetworks, m³/d
Each subnetwork's own catchment, m³/d: the plots that load its manholes, no transfer from an upstream subnetwork, no peaking. 2070 is saturation. Same for every option.
Subnetwork | Plots | 2024 | 2025 | 2030 | 2035 | 2040 | 2045 | 2050 | 2055 | 2060 | 2065 | 2070 | Sewer length, km | Infiltration m3d
O1 | 8948 | 3712.1 | 3820.4 | 4452.5 | 5137.6 | 5931.8 | 6624.3 | 7445 | 8431.8 | 8730.4 | 9370.1 | 9371 | 207 | 149
O2 | 4783 | 4633.7 | 4665 | 4847.4 | 5045.2 | 5274.4 | 5474.4 | 5711.3 | 5996.3 | 6058.7 | 6059.5 | 6060.3 | 116.8 | 84.1
O3 | 11287 | 3874.8 | 4013.1 | 4819.9 | 5694.4 | 6708.2 | 7592.1 | 8639.7 | 9896.2 | 10707.2 | 10764.2 | 10775.3 | 265.2 | 191
O4 | 4707 | 1728.6 | 1763.8 | 1969.5 | 2192.3 | 2450.7 | 2675.9 | 2942.9 | 3261.5 | 3636.5 | 3782.5 | 3782.5 | 121.8 | 87.7
O5 | 1273 | 105 | 116.6 | 184.3 | 257.6 | 342.7 | 416.8 | 504.7 | 609.6 | 733.8 | 836.8 | 981.4 | 28.4 | 20.5
O6 | 909 | 410.5 | 414.6 | 438.4 | 464.2 | 494 | 520.1 | 551 | 588 | 631.7 | 681.7 | 772.1 | 33.2 | 23.9
O7 | 2397 | 546.5 | 559.7 | 636.2 | 719.2 | 815.4 | 899.3 | 998.8 | 1116.9 | 1256.2 | 1413.7 | 1597.7 | 43.5 | 31.3
O8 | 797 | 115 | 121.9 | 162.3 | 206.1 | 256.8 | 301 | 353.4 | 416 | 491.4 | 549.7 | 620.9 | 23.5 | 16.9
O9 | 18005 | 1271.8 | 1307 | 1512.3 | 1734.8 | 1992.7 | 2217.6 | 2484.1 | 2802.5 | 5340.8 | 8727.4 | 11743.3 | 309.7 | 223
O10 | 1822 | 37.5 | 41.3 | 63.2 | 86.9 | 114.4 | 138.4 | 166.9 | 200.8 | 247.6 | 605.8 | 1160.2 | 36.6 | 26.3
O11 | 992 | 83.9 | 86.1 | 99.1 | 113.1 | 129.4 | 143.6 | 160.4 | 180.5 | 204.3 | 290.2 | 671.8 | 30.6 | 22
O12 | 1417 | 306.9 | 313 | 348.7 | 387.4 | 432.3 | 471.4 | 517.7 | 573 | 638.4 | 712.3 | 1350.6 | 49 | 35.3
O13 | 74 | 2.2 | 2.5 | 4.7 | 7.1 | 9.8 | 12.2 | 15.1 | 18.4 | 22.4 | 27 | 66 | 2.1 | 1.5
O14 | 377 | 137.8 | 138.9 | 145 | 151.6 | 159.2 | 165.9 | 173.8 | 183.2 | 201.8 | 217.7 | 331.4 | 12.2 | 8.8
O15 | 1466 | 33.3 | 52.3 | 163.2 | 283.4 | 422.7 | 544.2 | 688.2 | 861.4 | 1050.2 | 1155.3 | 1155.3 | 13.1 | 9.4
O16 | 1891 | 128.8 | 132.4 | 153.9 | 177.1 | 204 | 227.5 | 255.3 | 288.5 | 327.7 | 490.5 | 1144.4 | 13.1 | 9.4
O17 | 665 | 38.8 | 41.9 | 60.2 | 80 | 102.9 | 122.9 | 146.6 | 174.9 | 208.3 | 283.7 | 454.7 | 8.3 | 6
O18 | 567 | 26.4 | 28.7 | 41.9 | 56.3 | 73 | 87.5 | 104.7 | 125.2 | 149.5 | 198.6 | 330.1 | 5.5 | 4
O19 | 384 | 183.7 | 184.9 | 192.1 | 200 | 209 | 217 | 226.3 | 237.5 | 250.7 | 277.5 | 349 | 8.2 | 5.9
O20 | 352 | 170.6 | 171.5 | 176.8 | 182.6 | 189.3 | 195.1 | 202 | 210.3 | 220 | 280.8 | 291.4 | 9.8 | 7.1
O21 | 4384 | 1815.6 | 1850.1 | 2051.5 | 2269.8 | 2522.8 | 2743.5 | 3004.9 | 3298.1 | 3529.5 | 3808.7 | 3996.3 | 107.2 | 77.2
O22 | 523 | 29.5 | 31.9 | 46.1 | 61.5 | 79.3 | 94.9 | 113.3 | 135.3 | 161.2 | 193.6 | 306 | 11.2 | 8.1
O23 | 250 | 8 | 9 | 15 | 21.4 | 28.9 | 35.4 | 43.1 | 52.2 | 63.1 | 76.6 | 123.6 | 11.5 | 8.3
O24 | 1677 | 943.4 | 965.3 | 1093.2 | 1231.8 | 1392.4 | 1532.5 | 1698.5 | 1898.3 | 1942 | 1942 | 1942 | 30.9 | 22.2
outside the 24 | 7318 | 507.4 | 512.1 | 539.1 | 568.3 | 602.2 | 631.8 | 666.9 | 709.4 | 719.4 | 720.3 | 721.5 | 0 | 0
Total | 77265 | 20852 | 21344 | 24216.3 | 27329.3 | 30938.4 | 34085.2 | 37814.5 | 42265.8 | 47523.1 | 53466.4 | 60098.8 | 1498.3 | 1078.8
Infiltration: 720 L/d per km of sewer (PAM-GUD-201, page 72) on the subnetwork's active sewer length; not included in the flow columns, add it where the design needs it.
'outside the 24': plots whose nearest manhole is inactive (the three deactivated absorption-well areas); not carried by any subnetwork, listed so the total reconciles.

## Population
Population of the 24 subnetworks
Each subnetwork's own catchment, people: the plots that load its manholes, no transfer from an upstream subnetwork, no peaking. 2070 is saturation. Same for every option.
Subnetwork | Plots | 2024 | 2025 | 2030 | 2035 | 2040 | 2045 | 2050 | 2055 | 2060 | 2065 | 2070
O1 | 8948 | 22618 | 23249 | 26939 | 30940 | 35579 | 39620 | 44413 | 50172 | 51916 | 55650 | 55655
O2 | 4783 | 26188 | 26371 | 27437 | 28590 | 29928 | 31097 | 32478 | 34143 | 34508 | 34513 | 34517
O3 | 11287 | 22558 | 23366 | 28077 | 33181 | 39100 | 44261 | 50378 | 57714 | 62450 | 62782 | 62847
O4 | 4707 | 10345 | 10552 | 11751 | 13053 | 14560 | 15876 | 17435 | 19295 | 21485 | 22337 | 22337
O5 | 1273 | 648 | 716 | 1111 | 1540 | 2036 | 2468 | 2982 | 3594 | 4319 | 4921 | 5765
O6 | 909 | 2340 | 2364 | 2503 | 2653 | 2828 | 2980 | 3160 | 3376 | 3632 | 3924 | 4451
O7 | 2397 | 3189 | 3265 | 3712 | 4197 | 4759 | 5248 | 5829 | 6518 | 7332 | 8251 | 9326
O8 | 797 | 674 | 714 | 950 | 1205 | 1502 | 1760 | 2066 | 2431 | 2871 | 3212 | 3628
O9 | 18005 | 6248 | 6452 | 7650 | 8953 | 10460 | 11770 | 13326 | 15184 | 30006 | 49778 | 67383
O10 | 1822 | 233 | 256 | 384 | 521 | 680 | 822 | 989 | 1188 | 1459 | 3550 | 6788
O11 | 992 | 528 | 542 | 617 | 698 | 793 | 876 | 975 | 1093 | 1230 | 1731 | 3960
O12 | 1417 | 1722 | 1758 | 1966 | 2192 | 2454 | 2682 | 2953 | 3276 | 3658 | 4089 | 7816
O13 | 74 | 16 | 18 | 30 | 44 | 60 | 74 | 91 | 111 | 134 | 160 | 388
O14 | 377 | 718 | 724 | 759 | 798 | 843 | 881 | 927 | 983 | 1091 | 1185 | 1848
O15 | 1466 | 237 | 347 | 994 | 1696 | 2510 | 3220 | 4059 | 5072 | 6173 | 6786 | 6786
O16 | 1891 | 792 | 812 | 939 | 1074 | 1231 | 1369 | 1530 | 1724 | 1953 | 2904 | 6721
O17 | 665 | 242 | 259 | 366 | 482 | 616 | 733 | 871 | 1036 | 1231 | 1671 | 2670
O18 | 567 | 168 | 183 | 258 | 342 | 440 | 524 | 626 | 746 | 887 | 1174 | 1941
O19 | 384 | 944 | 951 | 994 | 1039 | 1092 | 1138 | 1193 | 1258 | 1335 | 1491 | 1909
O20 | 352 | 459 | 464 | 495 | 529 | 568 | 602 | 642 | 691 | 747 | 1102 | 1164
O21 | 4384 | 9892 | 10093 | 11269 | 12544 | 14020 | 15308 | 16835 | 18547 | 19898 | 21528 | 22623
O22 | 523 | 196 | 210 | 293 | 382 | 487 | 578 | 686 | 813 | 965 | 1154 | 1810
O23 | 250 | 0 | 6 | 41 | 78 | 122 | 160 | 204 | 258 | 322 | 401 | 675
O24 | 1677 | 5944 | 6072 | 6818 | 7628 | 8566 | 9383 | 10354 | 11519 | 11773 | 11773 | 11773
outside the 24 | 7318 | 2995 | 3022 | 3180 | 3350 | 3548 | 3722 | 3925 | 4174 | 4233 | 4238 | 4245
Total | 77265 | 119893 | 122766 | 139535 | 157710 | 178781 | 197153 | 218926 | 244914 | 275608 | 310307 | 349029