Sultanate of Oman

Nama Water Services Company SAOC

Consultancy Services for Design and Supervision for STP, Sewer and TE Networks Systems in Ibri

Tender No. T/2719110/2025

Design Criteria

Sewer Network Design, Iteration W13

Revision 0

Renardet S.A. & Partners Consulting Engineers

Project 2621   ·   September 2026

# Document control

| Revision | Date | Status | Basis |
| --- | --- | --- | --- |
| 0 | 7 September 2026 | For design use | Project design-criteria register, with the 12 m cover decision and the wadi rules checked against the guideline pages on 7 September 2026; values applied by the W13 design pipeline read from its criteria module on the same date |

This document is rebuilt from source on every revision. A revision that has been issued is not overwritten; the next revision is written to its own folder.

# Contents

Document control	2

Contents	3

1  Purpose, sources and how to read this document	5

1.1  Sources	5

1.2  Citation convention	5

1.3  Precedence	5

1.4  The W13 design and the column "Adopted in W13"	5

1.5  Vocabulary	6

2  Gravity sewer hydraulics	7

2.1  Minimum gradient by tractive force	7

3  Minimum and maximum gradients	8

4  Pipes	9

5  Depth, cover and corridors	10

5.1  The 12 m limit	10

6  Chambers	11

7  Property connections, riders and lateral sewers	12

8  Wadis, flood hazard and crossings	13

8.1  Crossing procedure	13

9  Layout rules for the network	15

10  Pumping stations	16

11  Force mains	18

12  Flow estimation	19

12.1  Two methods in the guideline, and which one governs	19

12.2  Population and occupancy	19

12.3  The load basis	20

12.4  Water demand	21

12.5  Wastewater generation	22

12.6  Peak factors, infiltration and tankers	22

12.7  Values applied in the W13 pipeline	23

13  Design life, horizons and climate	25

14  Treated effluent	26

15  Sewage treatment plant	27

16  Water and treated effluent networks	29

17  Odour and hydrogen sulphide	30

18  Modelling, options appraisal and project workflow	31

19  Surveys and investigations	32

20  Register of project decisions and assumptions	33

21  Deviations to be declared to NWS	35

Appendix A  Inception Report values against the guideline	36

# 1  Purpose, sources and how to read this document

This document sets out the design criteria for the Ibri sewer network. Every numeric value is taken from one of the three Nama Water Services design guidelines and cited to its page, or is a stated project decision or assumption recorded in Sections 20 and 21. No value has been taken from memory or from general practice.

## 1.1  Sources

| Code | Document | What it governs here |
| --- | --- | --- |
| G203 | PAM-GUD-203 Wastewater Design Guidelines, 201 pages | Gravity sewers, chambers, pumping stations, force mains, treatment plants, odour, surveys |
| G1 | PAM-GUD-201 General Design Guidelines, 152 pages | Population, demand and flow estimation, design life, options appraisal, wadi and road crossings, modelling |
| G2 | PAM-GUD-202 Water and TSE Design Guidelines v1.0, 177 pages | Treated effluent and water networks |
| Scope | Terms of Reference, Tender T/2719110/2025 | Design horizons, model years, deliverables, inverted siphons |
| R0 | Inception Report Revision 0 and its demand workbook, August 2026 | Project values already adopted, reconciled against the guideline in Appendix A |

## 1.2  Citation convention

A reference such as G203-p33 §4.6.3 means page 33, clause 4.6.3 of PAM-GUD-203. G1 and G2 refer to PAM-GUD-201 and PAM-GUD-202 in the same way. Page numbers are the printed page numbers of the guideline PDF.

Where the guideline's wording decides how a rule applies, the phrase is quoted. Shall and must are requirements. Recommended and should are guidance the design follows unless a stated reason exists not to. A value marked as a project decision or a project assumption is ours, not the guideline's, and is listed in the registers at the end.

## 1.3  Precedence

An NWS-approved demand calculation, if one exists, outranks the whole flow-estimation chain in Section 12. The domestic consumption values in the guideline are indicative and are to be validated by NWS before design. Where the guideline gives two methods, the one written as a requirement governs and the other is a labelled fallback; Section 12.1 sets this out.

## 1.4  The W13 design and the column "Adopted in W13"

The network design is developed in iterations. Iteration W13 is the current design. It is calibrated on a 5.51 km² test area in Ibri town, where it produces 1,415 chambers, 71.6 km of sewer, a deepest cover of 10.45 m and no pumping station. The design must reproduce that result after every change before it is extended to the 531 km² study area.

Where a criterion is implemented in the design pipeline, the value applied is shown in the column "Adopted in W13". A blank cell means the criterion applies at a later stage or to a system the pipeline does not yet design. Sections 15 to 19 concern the treatment plant, the treated effluent system, odour, modelling and surveys, and carry no such column.

## 1.5  Vocabulary

The guideline names the tertiary pipes property connection sewer, rider sewer and lateral sewer. The network hierarchy in the design uses Nama's as-built vocabulary of trunk main, sub main and lateral, read from the manhole identifiers of the built network. Where this document says lateral sewer it means the guideline's tertiary pipe; where it says lateral tier it means the lowest tier of the secondary network.

# 2  Gravity sewer hydraulics

Table 1   Hydraulic design criteria for gravity sewers (G203 §4.2, pages 24 to 28)

| Item | Guideline requirement or value | Reference | Adopted in W13 |
| --- | --- | --- | --- |
| Design method | Colebrook-White or Manning; licensed software approved by NWS. The scope names SewerGEMS | G203-p24 | Colebrook-White on the true internal bore; SewerGEMS as the referee model |
| Roughness, Colebrook-White | ks = 1.5 mm, all pipe sizes and materials | G203-p24, p28 | 1.5 mm |
| Kinematic viscosity | 1.141 × 10⁻⁶ m²/s at 15 °C, conservative basic design | G203-p25 | 1.141 × 10⁻⁶ m²/s |
| Self-cleansing velocity | 0.75 m/s at peak flow; 0.90 m/s preferred | G203-p26 | 0.75 m/s required at every pipe; 0.90 m/s reported |
| Maximum velocity | 3.0 m/s at design depth of flow | G203-p27, p29 | 3.0 m/s |
| Proportional depth at peak flow | d/D ≤ 0.65 for D ≤ 350 mm; d/D ≤ 0.50 for D > 350 mm | G203-p27 Table 10 | As guideline, threshold at 350 mm |
| Manning n | PVC and GRP 0.009 to 0.011; PE 0.009 to 0.015; cement-lined concrete 0.012 | G203-p23 Table 8 | 0.013 as the ks-equivalent for the SewerGEMS export |
| Minimum gradient method | "Steeper gradient calculated based on self-cleansing velocity and minimum tractive force methodology shall be adopted as minimum pipe gradient." The tractive-force method applies at network heads where 0.75 m/s cannot be reached | G203-p27 §4.2.2.1 | The steeper of Table 11 (Section 3) and Equation 1 |
| Early-phase low flows | Flow in the early development phases is below the design flow, with a clogging risk at low velocity; more frequent inspection and cleansing in that period | G203-p28 §4.2.6 | Self-cleansing verified at start-year flows; see Section 12.3 on the direction of accuracy |

## 2.1  Minimum gradient by tractive force

The guideline gives the tractive-force method of Mara, Sleigh and Taylor for the minimum gradient, with a proportional depth of 0.2 and a Manning n of 0.013 behind it. It gives no numeric design value of the tractive tension; that value is a project assumption to be confirmed with NWS.

Smin = K ⋅ τ1.23 ⋅ Q-0.461	(1)

| Symbol | Meaning | Unit |
| --- | --- | --- |
| Smin | Minimum gradient | m/m |
| K | 2.33 × 10⁻⁴ with Q in m³/s; 5.5 × 10⁻³ with Q in L/s | – |
| τ | Tractive tension; project assumption 1 Pa (Section 20) | Pa |
| Q | Design flow, floored at 1.5 L/s, Mara's minimum design flow (Section 20) | m³/s |

At the 1.5 L/s floor the tractive-force gradient is close to the Table 11 value for DN200, so the two methods meet at the network head. If NWS sets the tension at 2 Pa rather than 1 Pa, a large share of the smallest pipes need a steeper gradient; the sensitivity is run by substituting the value, not by editing the design.

# 3  Minimum and maximum gradients

Table 11 of the guideline gives the minimum gradient of the secondary network by diameter, computed with Colebrook-White at 0.75 m/s. The design pipeline reproduces these values from the Colebrook-White equation within 5 % before any design runs, as a check on the hydraulic code.

Table 2   Minimum gradients of the secondary network (G203-p29 Table 11)

| Nominal diameter (mm) | Minimum gradient (mm/m) | Minimum gradient (%) |
| --- | --- | --- |
| 200 | 5.00 | 0.500 |
| 250 | 3.75 | 0.375 |
| 315 | 2.70 | 0.270 |
| 400 | 2.05 | 0.205 |
| 500 | 1.55 | 0.155 |
| 600 | 1.25 | 0.125 |
| 700 | 1.00 | 0.100 |
| 800 | 0.85 | 0.085 |
| 900 and larger | 0.75 | 0.075 |

Table 3   Rules on gradient (G203-p29 §4.3.1; G203-p18 Table 5)

| Item | Guideline requirement or value | Reference | Adopted in W13 |
| --- | --- | --- | --- |
| Oversizing | No oversizing of a pipe to obtain a flatter slope; uniform slope between chambers | G203-p29 | Diameter chosen for the flow, never for the slope |
| Maximum gradient | Governed by the maximum velocity of 3.0 m/s | G203-p29 | 3.0 m/s |
| Construction tolerance | "The lines and level of any pipeline shall not deviate from that described in the contract by more than 20 mm and combination of such deviation shall not create a reverse gradient." At DN900 and above the minimum gradient is 0.75 mm/m, so 20 mm over a 120 m spacing is about 22 % of the available fall | G203-p29 §4.3.1 | A fall tolerance of 0.040 m, twice the 20 mm, is carried in the invert solver so a flat profile keeps its margin |
| Round gradient values | – | Project decision | Pipes are laid at round 0.05 % steps so the value on the drawing is the value the invert levels came from. A single pipe is rounded up; a whole run is eased down to the next round value, which leaves the far end slightly shallower and never deeper. Measured cost on the test area: 1.0 % more excavation, 0.12 m on the deepest chamber, no additional pumping station |
| Tertiary slopes | Property connection sewer 3 % to 10 %; rider sewer 1 % to 10 %; lateral sewer 1 % to 10 %. Table 11 applies to the secondary network only; its 0.5 % at DN200 is not a lateral-sewer value | G203-p18 Table 5 | 3 % minimum for property connections, 1 % for riders and lateral sewers, 10 % maximum |

# 4  Pipes

Table 4   Pipe diameters and materials (G203 §4.1 pages 21 to 23; §5 page 35)

| Item | Guideline requirement or value | Reference | Adopted in W13 |
| --- | --- | --- | --- |
| Minimum diameters | Property connection OD160; lateral sewer OD200 with a maximum length of 45 m; main sewer OD200 minimum | G203-p22 Table 6 | OD160 tertiary; DN200 minimum main; diameter series 200, 250, 315, 400, 500, 600, 700, 800, 900, 1000, 1200 |
| Secondary network range | 200 to 400 mm typical; 400 mm is not a mandatory ceiling | G203-p23 |  |
| Materials, main sewer 350 mm and larger | GRP, HDPE or lined reinforced concrete in open trench; GRP or HDPE for trenchless installation | G203-p22 | PVC-U through the OD series to 315 mm; GRP above |
| PVC-U size series | OD-designated series to 315 mm | G203-p23 Table 7 | As guideline |
| Trunk main definition | Diameter over 800 mm, length over 1,000 m without connections, upstream of the treatment plant or a main pumping station | G203-p35 |  |
| Trunk material above 600 mm | GRP, lined reinforced concrete, profile-wall HDPE | G203-p35 Table 14 |  |
| Internal bore for hydraulics | Plastic mains are OD-designated, so the bore is smaller than the nominal size | G203-p22 Table 6 | PVC-U taken as SDR34 (SN8): bore = OD × (1 − 2/34). GRP nominal size is the bore. The wall class is pending PAM-SPC-207 (Section 20) |
| Crown-to-invert height | – | Project assumption | Outside diameter used for the geometry, nominal for GRP; a 0.05 m allowance for wall and bedding below the crown cover |

# 5  Depth, cover and corridors

Table 5   Cover and clearance (G203 §3.5 page 19; §4.6 pages 32 and 33)

| Item | Guideline requirement or value | Reference | Adopted in W13 |
| --- | --- | --- | --- |
| Minimum cover, gravity sewer | "The minimum depth for sewer pipes shall be 1.3 m to the crown" | G203-p33 §4.6.3 | 1.3 m to crown |
| Reduced cover | "If circumstances require installation of a pipe with depth less than 1.3 m above the crown, then concrete protection is required. The minimum cover above the pipe and its protection shall be 0.5 m." The exception needs a stated circumstance, concrete protection, and the 0.5 m measured above the protection | G203-p33 §4.6.3 | Not used |
| Property connection cover | 600 mm minimum | G203-p19 | 0.60 m |
| Maximum cover | "The recommended maximum cover for sewer pipes is approximately 10 – 12 m. Depths with cover greater than this shall be investigated with pipe manufacturers … Where the cost of excavation becomes prohibitive the Engineer shall incorporate pumping stations into the design." | G203-p33 §4.6.3 | 12.0 m of cover as a limit with no exception, checked at every chamber and along the trench between chambers (Section 5.1) |
| Horizontal clearance to other utilities | 3 m | G203-p33 |  |
| Service corridor widths | DN200 to 500: 2.0 m; 600 to 900: 2.8 m; 1000 to 1200: 3.2 m; 1400 to 1700: 4.0 m; 1800: 4.1 m; 2000 to 2400: 4.4 m | G203-p32 Table 13; p35 Table 15 |  |
| Position in the carriageway | At least 1 m from the kerb line, stated for force mains | G203-p51 | Applied to gravity sewers by inference; chambers at least 0.5 m from the kerb (Section 20) |

## 5.1  The 12 m limit

The guideline makes the cost of excavation, not the depth itself, the trigger for a pumping station, and treats 10 to 12 m of cover as a recommendation to be checked with pipe manufacturers. No cost analysis exists at concept stage, so the design applies 12 m of cover as a limit with no exception. Where a gravity sewer would pass 12 m, a pumping station is placed before that point, the sewage is lifted, and the sewer restarts at normal cover.

The limit is revisited only when the cost analysis exists, and then for each excursion on its own economics, not as a blanket relaxation. Pumping stations are not removed by digging deeper: the route is searched again first, and whatever pumping remains is real.

# 6  Chambers

Table 6   Chamber criteria (G203 §4.4 pages 29 to 31)

| Item | Guideline requirement or value | Reference | Adopted in W13 |
| --- | --- | --- | --- |
| Maximum spacing | DN200 to 315: 100 m; DN350 to 900: 120 m; DN1000 to 1400: 150 m; above DN1400: 200 m. Deviation needs NWS pre-approval | G203-p30 Table 12 | Runs split at 100 m, which satisfies every class; spacing rounded to 10 m, with 5 m as the fallback |
| Locations | Change of gradient or diameter, junctions, end of laterals, and at the regular spacing | G203-p29 | As guideline |
| Backdrop | Required where the invert drop exceeds 600 mm; external; maximum height 2 m, beyond which a vortex drop shaft; internal only in a chamber of 1.5 m diameter or more | G203-p30 | Drop trigger 0.60 m; backdrop maximum 2.0 m |
| Inlet angle | At least 90° to the direction of flow ("shall") | G203-p30 | 85° minimum applied; an inlet sharper than 75° is flagged for a purpose-made chamber with a curved channel and is never fixed by adding a chamber. Stated deviation, Section 21 |
| Minimum separation of chambers | None stated in any of the three guidelines | – | 3.0 m as a physical convention; two chambers closer than 3 m become one structure |
| Chamber size | "Sufficient size"; no table given | G203 §4.4 | DN1000 to 3 m depth, DN1200 to 6 m, DN1500 deeper; no hydraulic effect at concept |
| Prohibited locations | Wadis and flood-prone or washout areas, for pipelines and chambers alike | G203-p30 §4.4.1; p33 | Flood hazard classes 4, 5 and 6 excluded (Section 8) |
| Outlets per structure | – | Project convention | One physical outlet per chamber. A branch leaving a chamber that already has an outlet starts at the next house connection, or 10 m away |
| Clearance from plots | – | Project decision | Every chamber is checked against every plot boundary and slid clear; a corner chamber must be 2 m clear of any plot (Section 9) |

# 7  Property connections, riders and lateral sewers

The tertiary layer connects each property to the network. At concept stage its only hydraulic test is whether the property can drain by gravity to the sewer in its street; the pipes are not sized.

Table 7   Tertiary criteria (G203 §3, pages 17 to 22)

| Item | Guideline requirement or value | Reference | Adopted in W13 |
| --- | --- | --- | --- |
| Property connection sewer | OD160; slope 3 % to 10 %; cover 600 mm minimum; maximum length 50 m | G203-p22 Table 6; p18 Table 5; p19; p18 Table 4 note | As guideline |
| Rider sewer | Slope 1 % to 10 %. "Several HCC (usually up to 3) may be connected together by one or several Rider Sewers within the public ROW." | G203-p18 Table 5; p19 §3.4 | Up to 3 house connections per rider; the rider runs along the frontage in the public right of way; a lone house connects by a lateral sewer without a rider |
| Lateral sewer | OD200; slope 1 % to 10 %; maximum length 45 m. Table 6 states the 45 m on the lateral sewer row only, while §3.2 attaches it to rider and lateral alike | G203-p22 Table 6; p17 §3.2 | 45 m applied to riders and lateral sewers, the conservative reading, as a declared project cap |
| Connection point | – | Project decision | The perpendicular projection of the plot onto the corridor it fronts, never the plot centroid; the connection is a short perpendicular spur; the plot loads the reach it fronts |
| Gravity viability check | – | Project assumption | The house drain leaves the plot 0.60 m below plot ground and is checked against the pipe invert interpolated at the connection chainage, at a blended fall of 2 % |
| Stub-outs | – | Project doctrine | A capped connection at the frontage of every planned plot, sized for its saturation flow; DN200 minimum usually governs |
| Output layers | – | Project decision | House connections and riders sit in their own layers in every output, never in the mains layer |

# 8  Wadis, flood hazard and crossings

Table 8   Wadi rules (G203 pages 30, 33 and 52; G203 §11.5.3.1)

| Item | Guideline requirement or value | Reference | Adopted in W13 |
| --- | --- | --- | --- |
| Pipelines and chambers in wadis | "Locating pipelines and associated chambers in wadis or areas subject to washout during heavy storms must be avoided." Page 33 repeats it as "shall be avoided" | G203-p30 §4.4.1(a); p33 | The design avoids it. Where no other route exists, the presence is a recorded and justified exception carried to the deliverable, never a silent one (project decision, 7 September 2026) |
| What counts as wadi ground | Areas subject to washout during heavy storms | G203-p30 | Classes 4, 5 and 6 of the 50-year flood hazard grid, which are flood-hazard classes keyed on danger to people and vehicles standing in for the washout criterion; classes 1 to 3 and cells with no value are dry. Project assumption, to be settled by a scour-depth check (Section 20) |
| Cover at a wadi crossing | 1.5 m to crown, gravity sewer and force main alike. The clause opens "As for gravitational sewer, the minimum cover should be…" and lists 1.3 m unprotected, 0.5 m protected and 1.5 m at a wadi crossing | G203-p52 §8.2.4 | 1.5 m |
| Reduced cover at a crossing | Whether the 0.5 m protected exception is available at a wadi crossing is not stated | G203-p33; p52 | Not available: the 1.5 m answers scour and concrete encasement answers external load. Project position, recorded as ours |
| Twin pipelines at an obstacle crossing | Allowed with a dedicated hydraulic justification: 0.75 m/s in all modes, mechanically independent restraint | G203-p52 §8.2.3 |  |
| Inverted siphons | "Inverted siphons shall not be allowed." The scope says avoid, and only where no other feasible means exists | G203-p182 §11.5.3.1(c); scope p12(60) | None. Any siphon is a formal deviation needing justification |
| Trenchless at major crossings | An alternative subject to NWS approval; settlement is decisive | G203-p21, p35 | Every dual-carriageway crossing is assumed trenchless (Section 9) |
| Treated effluent discharge to a wadi | Class A at least under MD 145/93; Environmental Authority and APSR approval | G203-p73 |  |

## 8.1  Crossing procedure

Running along a wadi and crossing one are different questions. The general guideline sets the procedure for a crossing.

Table 9   Wadi, road and falaj crossings (G1 §9.3, pages 85 and 86)

| Item | Requirement or value | Reference |
| --- | --- | --- |
| Data and approvals | Wadi bed profiles and cross-sections, flood frequency at 1 in 20, 1 in 50 and 1 in 100 years, bed material and bed-level change, from the Civil Aviation Authority and the Ministry of Agriculture, Fisheries and Water Resources; MoAFWR approval required | G1-p85 |
| Pipe material | Ductile iron over the crossing length plus 15 m each side, with mechanical or detachable joints | G1-p86 |
| Protection | NWS standard drawing PAM-STD-404; anti-flotation check with the pipe empty under flood or high groundwater | G1-p86 |
| Cover in soft soil | 2.0 m minimum | G1-p86 |
| Valves | Isolation and air valves on both sides of an active or major crossing; washout at the low point on one side; no chambers or markers in the wadi bed or embankments; everything accessible during a flood | G1-p86 |
| Road crossings | Trenchless preferred; reinstatement to the Oman Highway Design Manual | G1-p85 |
| Falaj crossings | Buffer zones, protection and minimum safe excavation distances; no-objection certificates sought at the preliminary stage | G1-p86; G203-p39 |

# 9  Layout rules for the network

The guidelines fix the hydraulics and the cover. They say little about where a sewer may run through a town. The rules below were set for this project from the road data supplied and from the shape of Nama's built network, and each states its basis.

Table 10   Layout rules and their basis

| Rule | Statement | Basis |
| --- | --- | --- |
| Road source | Corridors come from the road centreline layer. The dual attribute decides exclusion: 1 is a dual carriageway, 2 is a two-lane pair of which one side is used. Road class serves preference only, not exclusion: 150 national and arterial roads are single carriageways | Project decision, 19 August 2026 |
| Dual carriageways | No pipe of any kind runs along a dual carriageway, the trunk included, because the carriageway cannot be opened. Both lines of the pair are removed with their links and ramps. A line within 6 m and 25° of an excluded carriageway is treated as its twin and excluded too | Project decision, 19 and 20 August 2026 |
| Crossing a dual carriageway | Only as a short perpendicular pipe: within 25° of square, no longer than 70 m, trenchless, no chamber on the carriageway. The route search is charged 2,500 m of equivalent route for every crossing, and nothing within 30 m of a known underpass, so a crossing is used only where it pays | Project decision, 20 August 2026; trenchless per G1-p85 |
| Two-lane pairs | One side only, held for the whole corridor: the side with more fronting plots, tie-broken by lower ground. Plots on the far side connect by a direct link at the road end | Project decision, 19 August 2026 |
| Roundabouts | Carry no sewer; the approach legs terminate at the ring. A ring is a roundabout only if no plot lies inside it, every node has an approach arm and the arcs are curved, with a perimeter under 150 m and an equivalent radius under 30 m | Project decision, 19 August 2026 |
| Traffic links | Turning fillets, slip roads and diagonal links between carriageways exist for vehicles; the sewer joins at a point. A link is dropped when it serves no plot within 40 m, both ends are attached, the way round is no more than three times its length, and it is short (120 m or less) or strongly curved (45° or more). Dead-ends serving no plot are removed, repeatedly | Project decision, 19 and 20 August 2026 |
| One line per street | A straight street between two intersections is one polyline; a break of less than 10° is dissolved | Project decision |
| Head of a run | A run starts at the first house gate on the street, taken as the plot centroid dropped square onto the street and searched up to 45 m, not at the street end | Project decision, 20 August 2026 |
| Chambers at bends | Up to 5°: none, the joint deflection absorbs it. 5° to 45°: one chamber at the bend. A sweeping curve over 45°: two or three chambers breaking it into chords, three only on a wide long bend. A corner chamber sits at the intersection of the tangents only if it is 2 m clear of every plot boundary; otherwise the curve is followed. The governing constraint is cleaning access, not pipe flexibility | Project decision, 19 August 2026 |
| Hierarchy | Trunk main, sub main and lateral, in Nama's as-built vocabulary; every pipe carries its tier. Each join onto the main pipe is charged 400 m of equivalent route, so only collectors reach it: 20 joins on the test area, where fewer than 15 costs a pumping station and fewer than 8 starts crossing dual carriageways | Learned from the built network, 23 August 2026 |
| Main pipe | An input drawn by the engineer, not derived: both legs drain to their meeting point and on to the existing treatment plant | Project input, 20 August 2026 |
| Pumping pockets | A pocket of fewer than 50 plots is absorbed at detail design. The rules for cascading stations and for sizing a rising main on pump duty are not settled and will be decided when the design raises them | Project position, 7 September 2026 |

# 10  Pumping stations

The test area needs no pumping station. The criteria below apply wherever the 12 m limit of Section 5.1 places one in the wider study area.

Table 11   Pumping station criteria (G203 §7, pages 38 to 49)

| Item | Requirement or value | Reference |
| --- | --- | --- |
| Siting | Hydraulics-driven; flooded suction preferred; the force-main energy-economic study determines the optimal location. The site is approved in advance by NWS at concept or preliminary stage | G203-p38 §7.2 |
| Flood protection | Pump pedestal, building floor, transformers, substation and emergency generator above the maximum flood level; floors at least 300 mm above the 1 in 50 year flood level; surface and stormwater designed for a 1 in 50 year return period; sites under power lines avoided | G203-p38 §7.2 |
| Station type | Type 1 up to 100 L/s, one duty and one standby; Type 2 over 100 to 300 L/s, two duty and one standby; Type 3 over 300 L/s, three duty and one standby. Pumps rotate duty each cycle; station pipework 0.6 to 2.5 m/s (0.5 m/s with a grinder); motor speed at most 1,450 rpm above 5 L/s and 2,800 rpm at or below; solids passage 76 mm minimum, 65 mm with an upstream basket | G203-p40 to 41 Table 17 |
| Small stations | At least two identical pumps, duty and standby, each at 100 % of design flow; peak flow achievable with any one unit out | G203-p39 |
| Land area | Type 1: 50 to 100 m²; Type 2: 200 to 400 m²; Type 3: 900 m² or more; access with a turning circle at least 6 m wide and hard standing | G203-p43 Table 21 |
| Design life | Non-structural mechanical installations 20 years; Table 17 rates pumps at 15 years, which is the figure for pump replacement in the life-cycle cost | G203-p38; p40 Table 17 |
| Minimum-flow factors | Initial minimum flow = average flow × factor: 50 L/s → 0.25; 500 L/s → 0.35; 2,500 L/s → 0.45; 5,000 L/s → 0.50. This flow, not the average, sizes the force main against deposition | G203-p40 §7.4 Table 16 |
| Emergency overflow | Every pumping station shall have one, with Environmental Authority approval; never at an upstream manhole; wet-well overflow with dip tube or baffle; storage above the start level of the last duty pump. Prevention by dual power supply, trunk or basin storage, emergency storage and emergency pumping | G203-p46 to 47 §7.5 |
| Wet-well volume | Minimum live volume per Equation 2, with successive start and stop levels 200 to 300 mm apart, a 5 to 10 s start delay, and CFD plus physical modelling for stations of 0.5 m³/s or more | G203-p48 §7.8 |
| Net positive suction head | Equation 3, with a margin of at least 1 m | G203-p47 §7.6 |
| Hydrogen sulphide at the force-main outlet | Where H₂S is expected and no field data exists, design for management and monitoring at 50 to 100 ppm average and 200 ppm peak at the pressure-main termination; monitoring at the termination manhole controls chemical injection at the force-main start | G203-p47 §7.7; p55 §8.5 |
| Stakeholder approvals | No-objection certificates, including falaj crossings, sought at the preliminary stage | G203-p39 |

V = 0.25 ⋅ Q ⋅ T	(2)

| Symbol | Meaning | Unit |
| --- | --- | --- |
| V | Minimum live volume of the wet well | m³ |
| Q | Capacity of a single pump | m³/s |
| T | Cycle time, 3600 divided by the starts per hour; at least 10 starts per hour for motors up to 30 kW | s |

NPSHa = Ha - Hvpa - Hst - Hf	(3)

| Symbol | Meaning | Unit |
| --- | --- | --- |
| NPSHa | Net positive suction head available; margin of at least 1 m over the pump's requirement | m |
| Ha | Atmospheric pressure head | m |
| Hvpa | Vapour pressure head of the liquid | m |
| Hst | Static suction lift | m |
| Hf | Friction loss in the suction pipework | m |

# 11  Force mains

Table 12   Force main criteria (G203 §8, pages 50 to 55; G1 Appendix III)

| Item | Requirement or value | Reference |
| --- | --- | --- |
| Minimum velocity | 0.75 m/s continuous, maintained at the design minimum flow of Table 16 under maximum static head; 1.0 m/s intermittent; 1.2 m/s in vertical pipework | G203-p50 §8.1; p40 Table 16 |
| Maximum velocity | 2.5 m/s | G203-p50 |
| Minimum diameter | 75 mm bore for non-clog pumps; 50 mm bore for grinder pumps | G203-p50 §8.1 |
| Gradients | At least 1 in 500 rising and 1 in 300 falling; never flatter than 1 in 750 | G203-p50 §8.2.1 |
| Run full | Designed to run full and remain full at all times | G203-p51 §8.2.1 |
| Retention time | Ideally 30 minutes or less; air valves at high points and washouts at low points | G203-p50 |
| Access | Every 500 m | G203-p50 |
| Valve spacing | In-line isolation valves at about 500 m and never more than 800 m; washout valves at low points sized to empty a section in 3 to 4 hours (main up to 400 mm: 100 mm; 500 to 800 mm: 150 mm; 900 to 1,200 mm: 200 mm; 1,200 mm and larger: 300 mm); double-orifice air valves at high points with the approach no flatter than 1 in 500 and the departure no flatter than 1 in 300, each with its own geared isolation valve | G203-p53 to 54 §8.4 |
| Separation from water mains | 3.0 m horizontal; crosses under the water main with 450 mm vertical clearance outside to outside; one full length of water pipe centred so both joints are as far from the force main as possible; structural support where required | G203-p51 §8.2.2 |
| Layout | Straight lines, sharp bends avoided, at least 1 m from the kerb line in a carriageway | G203-p51 |
| Material, in the station | Ductile iron recommended; stainless steel for stations under 100 L/s | G203-p52 §8.3 |
| Material, pressure main | "The recommended pipe material for the pressure main is Ductile Iron and HDPE" | G203-p53 §8.3 |
| Termination | Discharge to the gravity system at a manhole, entering not more than 300 mm above the receiving flow line; water seal and forced venting through odour control where turbulent; corrosion-resistant or lined receiving manhole | G203-p55 §8.5 |
| Surge analysis | Transient analysis in NWS-approved software; simultaneous pump start and stop modelled to N+1; no vapour cavities or column separation; minimum pressure not below the manufacturer's limit or 0.2 bar below atmospheric, whichever is higher; maximum not above the test pressure or the lowest component rating; a zero-roughness run first for the worst case | G1-p146 to 147 Appendix III |

# 12  Flow estimation

## 12.1  Two methods in the guideline, and which one governs

The general guideline gives two methods for almost every demand and flow parameter. The first is for planning and forecasting across broad service areas. The second is written as a requirement wherever detailed land-use information exists.

| Tier | Applies when | Method |
| --- | --- | --- |
| A, planning and forecasting | Broad service areas without land-use detail | G1 Table 11 consumption per head with the distributed ratios of 22 % and 14 %; G1 Table 19 return rates of 85 % and 54 % |
| B, project-specific design | "where detailed land use information is available" | G1 Table 12 unit rates for non-domestic and governmental demand; design flows to BS EN 752 or a stated equivalent, supported by site-specific evidence |

Three clauses carry the requirement. Non-domestic consumption "shall be calculated using the reference values presented in the Table 12" where the project provides detailed land use. Governmental consumption "is to be calculated specifically for the project and not as a ratio of domestic consumption". Design flows for project-specific designs "shall be calculated in accordance with a relevant international standard such as BS EN 752", and "calculations shall clearly state which standard has been used".

Every value from the planning tier that appears in a deliverable is labelled as a fallback pending the project-specific data, with the data request named. Section 12.3 records the load basis adopted and the reason the G1 Table 12 method cannot yet be applied.

## 12.2  Population and occupancy

Table 13   Population criteria (G1 §7.2, pages 58 and 59)

| Item | Guideline requirement or value | Reference | Adopted in W13 |
| --- | --- | --- | --- |
| Official source | NCSI population and housing data at governorate, wilayat and settlement level | G1-p58 §7.2.1 | NCSI series carried in the Inception Report |
| Wilayat to settlement | Where forecasts exist only at wilayat level, distribution must follow the latest census settlement shares | G1-p58 | As guideline |
| Below settlement level | Pro rata to the number of electricity accounts, supplied by NWS | G1-p58 | 33,970 electricity accounts, each counted as a property |
| Extrapolation limit | NCSI forecasts cover 20 to 25 years. Beyond them a polynomial regression, but "it is not recommended to extrapolate more than ten years beyond the available forecast period" | G1-p58 | The 2055 and ultimate cases are defended on land capacity, not on the extrapolated curve |
| Population from plots | Equation 4. Occupancy rate = population ÷ housing units from NCSI, most recent data, at the geographic scale of the project | G1-p58 to 59 §7.2.2 | Properties per plot counted from electricity accounts, 1.46 domestic per matched plot; additional-account entries are separate dwellings |
| Occupancy rate | Population ÷ housing units | G1-p58 | Project basis 5.32 people per domestic property, measured as 2024 settlement population ÷ counted domestic properties over the same 25 settlements. The W13 test-area run carries 5.0, the value inherited from the design it was copied from; the full-area run is to apply 5.32 (Section 20) |
| Build-out | "special care must be given in cases of plot subdivision … development speed must be considered through appropriate phasing assumptions … development percentages must be applied over the design period … particularly avoiding overestimation" | G1-p59 note | Pipes and civil works sized on every plot at saturation; dated years use zone totals capped at the zone ceiling (Section 12.3) |

Population = Nplots × nprop × OR	(4)

| Symbol | Meaning | Unit |
| --- | --- | --- |
| Nplots | Number of plots in the area | – |
| nprop | Average properties per plot; counted from electricity accounts, 1.0 only as the fallback for a plot with no account | – |
| OR | Occupancy rate, people per property | – |

The occupancy rate departs from the guideline's definition in one respect. Housing units are not published at settlement level, so properties counted from electricity accounts stand in for them. The figure was validated by coverage: the 25 settlements hold 63.4 % of the wilayat population, and at 5.32 the wilayat implies 34,504 domestic properties against 22,588 held, which is 65.5 %. The two agree within 2.0 points, so 5.32 is a measurement rather than a coverage artefact. It is listed as a deviation in Section 21.

## 12.3  The load basis

The load basis was fixed on 30 August 2026 and is applied without variation. The planning-tier ratios set the volume; land use sets where that volume is placed. The two do not overlap, so the method neither mixes tiers nor double counts.

1.   Domestic load = counted domestic accounts × occupancy rate × consumption per head × return rate.

2.   Non-domestic and governmental volume = 22 % and 14 % of the domestic volume, the distributed ratios for Adh Dhahirah (G1-p60 Table 11).

3.   That volume is placed on the commercial and government plots identified by account tariff. It is not spread across the population, so a residential-only branch carries no commercial flow.

4.   G1 Table 12 is not applied. It is priced in pupils, beds, employees and floor area, and none of these have been supplied, so the condition in §7.3.2 is unmet in substance. It is adopted the day real quantities arrive, and never together with the ratios.

Four streams sit outside the ratios and are added separately, because the guideline excludes them by name: identified projects such as the industrial estate, special consumption such as labour camps, potable and sewage tankers, and private wells and other non-network abstraction. Tanker water generates sewage at the same 85 % return rate as domestic supply.

Table 14   Rules within the load basis

| Rule | Statement | Basis |
| --- | --- | --- |
| Where the load goes | Every plot, built, planned and unparceled buildings alike, carries its full saturation load in the pipe and civil design, accumulated with the peak factor and with no timing. Dated years use zone totals only: the projection capped at the zone ceiling, with the surplus spilled to adjacent zones in proportion to their vacancy. The two meet only at trunk nodes | Project doctrine, 15 August 2026 |
| Phased elements | Treatment trains, pumps and force-main duty equipment are phased on the dated years; buried civil works are built for saturation | Project doctrine |
| Agricultural plots | An agricultural meter is an irrigation pump and generates no wastewater. On 172 of 319 agricultural plots Nama bills a household tariff alongside the farm tariff, so dwelling and pump are metered separately. An agricultural meter on a plot that already carries a domestic meter adds nothing; an agricultural-only plot carries no dwelling | Project decision, 30 August 2026, from the account data |
| Cost-reflective tariff accounts | 499 accounts on the cost-reflective tariff are a consumption class, not a land use. They are the largest consumers and cannot be classified by tariff alone; they are resolved against the plot layer or by site check before any ratio is applied | Open item |
| Direction of accuracy | One population figure cannot serve every use. Pipe sizing and plant staging fail on an under-estimate. Self-cleansing and the early cleansing schedule fail on an over-estimate: a pipe assumed to scour itself while it silts. Capacity is sized on the high case, the cleansing schedule on the low case, and the connection ratio of 0.51 in 2024 rising to 0.61 by 2028 is carried explicitly | G1-p72 §7.4.4 and the Inception Report |

## 12.4  Water demand

Table 15   Water demand criteria (G1 §7.3, pages 59 to 62)

| Item | Guideline requirement or value | Reference | Adopted in W13 |
| --- | --- | --- | --- |
| Domestic consumption, Adh Dhahirah | 164 L per head per day. Table 11 values are "indicative figures derived from the recent Integrated Master Plan (2024)", apply "in absence of any updated figures", and "should be validated by NWS as essential design criteria, before designing the project" | G1-p59 to 60 Table 11 | 164 L/head/day |
| What the figure measures | Network-accounted domestic water ÷ (occupancy × active domestic accounts). Tanker and private-well supply are not in it | G1-p60 | Tanker supply added separately (Section 12.5) |
| Non-domestic, project-specific method | G1 Table 12 unit rates: education 130 L/day per pupil and staff; hospitals 650 L/day per bed and staff; shopping 12.2 L/day per m²; hotels 200 to 500 L per guest per day; offices 93 L/day per employee; restaurants 7.4 L/day per m²; mosques 185 L/day per m²; dry industry 93 L/day per employee; army camps 185 L/day per occupant; prisons 185 L/day per prisoner and staff; wet industry not applicable, the developer supplies it | G1-p61 Table 12 | Not applied until the quantities are supplied (Section 12.3) |
| G1 Table 12 unit basis | Keyed to floor area, pupils, beds and employees, never to plot area. Applied to cadastral plot area the mosque rate alone gives about four times the whole ultimate plant flow | G1-p61 | Plot area is never substituted |
| G1 Table 12 deviations | "The designer can provide additional details per category or data for his design and shall substantiate the use of an alternative value" | G1-p61 note |  |
| Non-domestic, planning method | 22 % of domestic consumption; the column is headed "Distributed Non-Domestic Ratio (% LPCD)", a governorate water-balance volume spread over population. The ratio can be updated by the NWS planning department | G1-p60 §7.3.2 | 22 %, as the volume in Section 12.3 |
| Governmental | Project-specific: "not as a ratio of domestic consumption". Planning fallback 14 % | G1-p60 to 61 §7.3.3 | 14 %, as the volume in Section 12.3 |
| Special consumption | Labour camps and high-water industry must be provided by the developer; not covered by population forecasts | G1-p61 §7.3.4 | Additive, outside the ratios |
| Potable tanker demand | Where a tanker filling station is in or near the project area its consumption must be assessed from NWS filling-station data and added. Table 13: Adh Dhahirah 5,145 m³/day in 2021 to 2023, which is 333 % of the 2023 network domestic consumption, the highest in Oman. The master plan holds tanker demand constant | G1-p61 to 62 §7.3.5 Table 13 | Tier 1 data request |
| Double counting | G1 Table 12 or the ratios, never both | G1-p60 to 61 | Ratios only, until G1 Table 12 quantities arrive |

## 12.5  Wastewater generation

Table 16   Wastewater generation (G1 §7.4, pages 70 and 71)

| Item | Guideline requirement or value | Reference | Adopted in W13 |
| --- | --- | --- | --- |
| Return rate | Table 19: domestic and tanker 85 %; non-domestic, government and commercial, 54 % | G1-p70 to 71 §7.4.1 | 0.85 domestic |
| Project-specific design flows | To BS EN 752 or an equivalent standard, stated in the calculations, supported by site-specific evidence; the British Water Code of Practice for Flows and Loads is named as a guide | G1-p71 §7.4.1 |  |
| Other water sources | "the Designer shall carry out an assessment of other potential water sources within the project area, such as private wells, private water providers, or other non-network abstractions"; "A specific attention is to be taken for catchments covered with private wells" | G1-p70 §7.4, §7.4.1 | Tier 1 data request; with tanker water at 333 % of network consumption the network demand alone under-predicts the load |
| Components | Domestic, non-domestic, tanker discharges and special facilities | G1-p70 §7.4 | As guideline |

## 12.6  Peak factors, infiltration and tankers

Table 17   Peaking and allowances (G1 §7.4.2 to §7.4.5, pages 71 to 73)

| Item | Guideline requirement or value | Reference | Adopted in W13 |
| --- | --- | --- | --- |
| Peak factor, primary | Merrimack, Equation 5, "is to be used" for a catchment "having over 100 properties"; peak factor = Qpdf ÷ Qadf | G1-p71 §7.4.2 | Merrimack above 100 properties; below 100 the guideline gives no formula and the 100-property factor is held |
| Peak factor, alternative | Peltier, Equation 6, "the Average Daily Flow in this formula is in liters per second" | G1-p72 | Reported as a comparison; no decision rests on it |
| Peak factor cap | "It is recommended that the hourly peak factor should not exceed 5.0", a recommendation rather than a limit | G1-p72 note | Reported above 5.0, never truncated |
| Infiltration | New networks 720 L/day per km of sewer; existing inland networks 10 % of the wastewater flow; existing networks in groundwater or coastal zones up to 40 %. "Infiltration due to storm water is not considered." | G1-p72 §7.4.3 | 720 L/day/km assigned to each pipe by length, without a diurnal pattern; the order of peaking and infiltration is to be confirmed with NWS (Section 20) |
| Infiltration exemption | "Tanker or vacuum collection do not require to account for infiltration volume" | G1-p73 | Tanker flow carries none |
| Sewage tankers | "In 2024, the yellow tanker represented approximately 17 % of the total flow reaching the STPs of Nama WS", a company-wide observation. Collection capacity assumes the same coverage as the water supply, reaching 100 % by the end of the planning period; self-cleansing checked at initial operation. Tanker loads are higher than network effluent | G1-p73 §7.4.4 | 17 % is not used as a design allowance; the tanker stream is assessed from filling-station data |
| Treatment plant margin | 10 % "when designing new STPs", applied "over and above any redundancies in the design" | G1-p73 §7.4.5; G203-p65 Table 29 |  |

Qpdf = 2.65 ⋅ Qadf0.879	(5)

| Symbol | Meaning | Unit |
| --- | --- | --- |
| Qpdf | Peak daily flow | ML/day |
| Qadf | Average daily flow | ML/day |

PFWW = 1.5 + 1Qm	(6)

| Symbol | Meaning | Unit |
| --- | --- | --- |
| PFWW | Wastewater peak factor, Peltier form from the 2024 Integrated Master Plan | – |
| Qm | Average daily flow | L/s |

## 12.7  Values applied in the W13 pipeline

The pipeline sizes every pipe on the saturation load of the plots that drain to it. The per-plot flow is Equation 7.

Qadf,plot = OR × nprop × qww1000	(7)

| Symbol | Meaning | Unit |
| --- | --- | --- |
| Qadf,plot | Average dry-weather flow of one plot at saturation | m³/day |
| OR | Occupancy rate, people per property | – |
| nprop | Properties on the plot, counted from electricity accounts | – |
| qww | Wastewater generated per head per day | L/head/day |

Table 18   Flow values carried by the W13 pipeline

| Quantity | Value | Source |
| --- | --- | --- |
| Domestic water consumption | 164 L/head/day | G1-p59 to 60 Table 11 |
| Domestic return rate | 0.85 | G1-p70 to 71 Table 19 |
| Wastewater per head, area average | 171.3 L/head/day | 164 × 0.85 with the 22 % and 14 % uplifts; a residential-only branch generates 139.4 L/head/day |
| Occupancy rate in the test-area run | 5.0 | Inherited value; project basis is 5.32 (Section 12.2) |
| Properties per plot | Counted from 33,970 electricity accounts; 1.0 only where a plot has no account | Project data, 19 August 2026 |
| Infiltration | 720 L/day per km, unpeaked | G1-p72 §7.4.3 |
| Peak factor | Merrimack; held at the 100-property value below 100 properties | G1-p71 §7.4.2 |
| Peak factor above 5.0 | Reported, never truncated | G1-p72 note |
| Test-area result | Qadf 3,620 m³/day; peak 96 L/s | W13 pipeline, 7 September 2026 |

# 13  Design life, horizons and climate

Table 19   Design life and horizons (G1 §7.1 and §7.5; scope)

| Item | Requirement or value | Reference |
| --- | --- | --- |
| Planning life | 25 years, which "corresponds both to the ultimate design capacity of the project, as well as the period over which the NPV will be calculated for … comparing schemes" | G1-p57 §7.1 |
| Asset lifetimes | Civil and structures 50 years; mechanical 20; electrical 15 to 50; instrumentation, control and automation 15; pipework 50. "These asset lifetimes are used for financial asset depreciation calculations"; technical life may differ | G1-p57 Table 10 |
| Scope horizon | Completion plus 25 years, or ultimate saturation; model years start, 2030, 2055 and ultimate; projections at five-year intervals | Scope p3, p14 to 15 |
| Saturation | No more developable plots. Zone ceilings bite inside the design horizon; the whole boundary saturates around 2062 to 2070 | Project doctrine |
| Climatic design, inland | Peak shade temperature 55 °C; maximum daily average 50 °C; maximum yearly average 35 °C; metal in sun 85 °C; relative humidity to 100 %. "All equipment shall be rated for continuous operation under [these] ambient conditions … and performance guarantees shall be given at these conditions" | G1-p78 to 79 §7.5 Table 24 |
| Climate resilience | Assessed at a 50-year horizon even where the asset life is shorter, with an NWS-agreed climate model at both +2 °C and +4 °C scenarios, including changed flood frequency and intensity in site selection | G1-p33 §4.4 |

# 14  Treated effluent

Table 20   Treated effluent criteria (G1 §7.4.6 and §7.4.7, pages 73 to 78)

| Item | Requirement or value | Reference |
| --- | --- | --- |
| Production ratio | 95 % of the plant inflow | G1-p73 |
| Network loss | "For design purposes, a system loss of 10 percent of all produced TSE shall be assumed", so the deliverable volume is about 85.5 % of the plant inflow, not 95 % | G1-p76 §7.4.6.3(b) |
| Sizing basis | "The TSE system shall be sized to accommodate the peak demand experienced during the summer months." Seasonal factors as a share of summer: December to February 50 %; March to May and September to November 75 %; June to August 100 % | G1-p76 §7.4.6.4 Table 23 |
| Irrigation rates | Summer planting rates: shrubs 20 to 40, palms 120 to 165, other trees 40 to 80 L per plant per day; hedges 10 L per m per day; ground cover and seasonal flowers 10 and grass 12 L per m² per day; densities of 15 m for trees and 3 m for shrubs. Roads and junctions with mixed vegetation and no data: 10 L per m² per day, subject to Municipality approval | G1-p73 to 75 §7.4.6.2 Tables 21 and 22 |
| Large consumers | "Any consumer with an average daily demand larger than 500 m³/day is to be studied individually", with an irrigation pattern reflecting its actual settings; consumers with storage spread their demand over the storage hours | G1-p76 §7.4.6.4 |
| Sludge production | 0.25 kg per m³ treated, a master-plan baseline described as "a general guideline" and process-dependent | G1-p78 §7.4.7 |

# 15  Sewage treatment plant

Table 21   Treatment plant criteria (G203 §10, pages 63 to 74; G1 §4 and §6)

| Item | Requirement or value | Reference |
| --- | --- | --- |
| Size category | Small under 500; medium 500 to 20,000; large 20,000 m³/day and above. The ultimate Ibri flow places the plant in the large category | G203-p65 |
| Design horizon | At least 15 years, projected population plus industrial load | G203-p65 |
| Capacity basis | Average per-head consumption per the latest NWS Integrated Master Plan; a more realistic figure only as an NWS-accepted, designer-justified exception | G203-p65 §10.2.2.1 |
| Site selection | Table 27: accessibility, land and phasing, winds, geology and hydrology, topography to limit pumping, groundwater and flood protection at the 25 and 100 year levels, buffer from residential areas, life-cycle cost | G203-p63 to 64 |
| Flood criteria | 25 and 100 year flood levels; the plant fully operational during floods | G203-p63 Table 27(i) |
| Land footprint | Per m³/day: MBR 0.45 to 0.9 m²; MBBR 0.9 to 1.8; SBR 0.9 to 1.8; IFAS 1.2 to 2.5; conventional and extended aeration 1.8 to 3.6; constructed wetland over 10 m² | G203-p64 Table 28 |
| Built footprint | Total footprint of all structures at most 35 % of the allocated land; boundary setbacks at least 5 m | G1-p50 §6.4.2 |
| Buffer zones | Small and medium plants 500 m to residential and industrial; large plants 300 to 1,000 m from odour modelling on the 5 odour unit contour; small plants under 150 population equivalent 10 to 30 m; sewage pumping stations 30 m residential and 20 m industrial. Subject to NWS approval and the environmental and social impact assessment | G1-p43 to 44 §6.1.3.3 Table 8 |
| Incoming flow | Average sewage flow plus infiltration plus a 10 % operational allowance. Hydraulic pass-through sized on the peak hourly flow; biology on the annual average flow and load. "The hydraulic and load design shall include recycled liquors and the received tanker volumes if applicable"; a design peak instantaneous flow is also defined | G203-p65 to 66 Table 29, §10.2.2.1 |
| Process lines | "Treatment plants shall be designed using several process lines allowing additional capacity for different design horizons or phases" | G1-p53 §6.6.2 |
| Redundancy | Modular N+1 at site level: N elements meet average-day flows, N+1 meets peak capacity | G1-p33 §4.3 |
| Organic load | At least 60 g BOD₅ and 80 g TSS per head per day unless justified; COD to BOD 1.8 to 2.2 for domestic sewage | G203-p74 |
| Existing works | For the upgrade or expansion of an existing plant the organic design rests on the measured strength from the client's laboratory records, with a growth increment | G203-p74 §10.3.1 |
| Raw sewage characteristics | Primarily from NWS laboratory data for the catchment. Table 30 defaults, usable only by NWS agreement: BOD₅ 350 to 400, COD 700 to 900, TSS 400 to 500, TKN 60 to 80, ammonia nitrogen 40 to 50, total phosphorus 10 to 15 mg/L, 20 to 35 °C. Table 31 tanker sewage: BOD 350 to 1,050, COD 1,350 to 5,000, TSS 900 to 4,300 mg/L | G203-p67 Table 30; p68 Table 31 |
| High-strength influent | Above a COD to BOD ratio of 2.2 the influent is "not effectively biologically treatable" and a separate treatment line is required where the volume is significant; the tanker stream triggers this | G203-p74 §10.3.1 |
| Organic peak factors | BOD and COD 1.5 for a small plant and 1.2 for medium and large; TKN 2.0 and 1.5; equalisation considered where surge loads are critical | G203-p74 §10.3.1 |
| Tanker reception | A dedicated tanker discharge station with screening and oil and grease removal; a flow-equalisation tank specifically for tanker discharge; the 48 to 72 hour emergency lagoon where NWS requires it; pre-acceptance sampling, procedures, traceability and contractual limits. Pre-treatment selected for tanker and non-domestic sewage | G203-p73 §10.3.1; G1-p55 §6.8 |
| Emergency lagoon | 48 to 72 hours of plant capacity "in specific cases, under NWS requirement and approval", for holding problematic influent or effluent and returning it to the inlet works; distinct from the scope's five-day storage lagoons | G203-p73; scope p13(61) |
| Effluent quality | "At least Class A" under MD 145/93 for wadi discharge, subject to prior agreement with NWS and to Environmental Authority and APSR approval. The MD 159/2005 nitrogen and phosphorus limits apply only "if the Wadi discharges to sea at a reasonable distance"; Ibri's wadis are inland | G203-p72 to 73 §10.2.4.3 |
| Nitrogen and chlorine | Total nitrogen below 15 mg/L as N; chlorine residual at the plant outlet 0.3 to 1.0 mg/L, up to 3.0 mg/L permitted to allow decay along the treated effluent network | G203-p71 §10.2.4.1 |
| Nature-based treatment | Constructed wetlands are limited to works of about 500 m³/day | G203-p101 |

# 16  Water and treated effluent networks

Table 22   Network criteria from the water and TSE guideline (G2 §7 and §9)

| Item | Requirement or value | Reference |
| --- | --- | --- |
| Transmission velocity | 1.0 m/s or more and below 2.0 m/s; 1.5 m/s is the common practical peak over a 25-year horizon | G2-p103 to 104 |
| Head loss equations | Darcy-Weisbach for large pipes and high velocity, Hazen-Williams for small diameters; any other needs NWS hydraulic team approval | G2-p104 |
| Roughness with age | Ductile iron C 140 falling to 120 and ε 0.26 rising to 0.45 mm over 20 years; GRP C 150, ε 0.005 mm; HDPE C 150, ε 0.007 mm; PVC C 150, ε 0.0015 mm | G2-p104 Table 21 |
| Treated effluent penalty | Roughness 30 % higher and Hazen-Williams C 10 % lower than the potable values | G2-p104 note |
| Maximum linear head loss | Transmission below 5.0 m/km; distribution below 3.0 m/km | G2-p105, p136 |
| Distribution velocity | 0.4 m/s or more and below 1.5 m/s; below 0.4 m/s a water-quality or age model and proof of a 0.2 mg/L chlorine residual | G2-p136 |
| Distribution pressure | At least 1.5 bar at the worst point at peak hour; at most 4 bar; pressure stays positive under fire flow | G2-p137 |
| Distribution pipe material | PE100 up to 1,000 mm in the fixed outside-diameter series; ductile iron above 300 mm and at road and wadi crossings | G2-p138 |
| Pumping, storage and surge | Storage classes in §5, pumping station design with NPSH and transients in §6, surge analysis mandatory per §10 | G2-p53 onward, p70 onward, p144 |
| Tanker filling stations | Peak-hour factor 1.5 to 2.0 on average flow; at least two concurrent bays; 20 % reserve; at least 1 m³ per minute per bay at 2 to 4 bar | G2-p154 |

# 17  Odour and hydrogen sulphide

Table 23   Odour and hydrogen sulphide criteria (G203 §11, pages 162 to 191)

| Item | Requirement or value | Reference |
| --- | --- | --- |
| Designer deliverable | Designers of sewage networks, pumping stations and force mains shall provide NWS a dedicated hydrogen sulphide management evaluation, preventive (re-sizing, chemical injection) and corrective (monitoring, flushing, coatings, odour treatment) | G203-p162 §11.1 |
| Network design for odour | Retention times minimised, turbulence avoided, no over-sizing of trunk sewers, which creates deposition | G203-p166 §11.3.2; p168 §11.4.2 |
| Pumping and force mains | Avoided wherever gravity is feasible and cost-effective; hydraulic detention minimised, with twinned force mains considered at low flow; force-main discharges submerged where possible; the main allowed to drain back to the wet well between cycles; a partially-full main avoided | G203-p181 to 182 §11.5.3.1 |
| Risk assessment | Qualitative Fayoux scoring on temperature, residence time, velocity and redox (0 to 5 no risk, 5 to 10 low, 10 to 30 significant or certain), evaluated at maximum temperature and night-time flow. Quantitative Pomeroy-Parkhurst, with effective BOD = BOD₅ × 1.07^(T − 20) | G203-p185 Table 99; p186 §11.5.3.4 |
| Odour limits at the boundary | Urban or near residential 3 to 5 odour units per m³; industrial 10 to 15; rural or isolated 10 to 20. Compliance at the boundary wall: 5 odour units per m³ at sensitive receptors, 15 at industrial, with at least three continuous online electronic noses. MD 41/2017 and BS EN 13725:2022 | G203-p165 §11.3.1; p170 Table 90 |
| Odour treatment | Abatement assessment and dispersion modelling to justify the odour unit or its absence; in most cases multi-stage, bio-trickling filter plus chemical scrubber with carbon where needed, removing 99.95 % of hydrogen sulphide and 85 % of odour; N+1 redundancy on every odour control system | G203-p170 to 176 §11.5.2 |
| Network emergency storage | Retention basins sized for 24 hours of nominal flow, emptied by sewage tanker; relief sewers at 1.5 times nominal flow. Distinct from the plant's 48 to 72 hour emergency lagoon | G203-p191 §12.1.1 |
| Trade effluent | Non-domestic discharges to sewer comply with Appendix 3 of Royal Decree 115/2001, under a customer agreement with NWS and with NWS-validated pre-treatment where needed | G203-p20 §3.10 |

# 18  Modelling, options appraisal and project workflow

Table 24   Modelling and appraisal criteria (G1 §1.6, §11, §12 and §13; Appendix III)

| Item | Requirement or value | Reference |
| --- | --- | --- |
| Hydraulic model method | To the WaPUG/CIWEM Code of Practice and the US EPA SWMM manuals; modelled at design and again after construction; static, extended-period and surge models submitted to NWS after each design phase, including the final as-built model | G1-p144; p109 §13.4.2 |
| Calibration acceptance | Peak flow within 10 to 15 %; volume within 15 %; correct peak-arrival timing; pump run time within 10 % | G1-p145 Table 32 |
| Options appraisal | At least three options with equivalent function and reliability: one sustainability-led, one international best practice, one established local practice. Evaluated over 25 years at a 5 % discount rate unless NWS instructs otherwise; NWS sets the multi-criteria weights; options within 10 % on total cost are decided on sustainability | G1-p95 to 96 §12; p99; p106 |
| Options per system | Three for the sewer network, three for the treated effluent network, three for each treatment plant. Lifting stations are not a separate set: their number follows from each network layout. Seven criteria: total lifetime cost; sustainability; social development and in-country value; adaptability and resilience; operability; constructability; environmental impact. Sensitivity on the weighting, the discount rate and the input criteria | Project doctrine, 31 August 2026, on G1-p95 to 106 |
| Financial method | Net present value and life-cycle cost at 5 % over 25 years decide; payback is reported but does not decide. The guidelines state the requirement and not the method, so ISO 15686-5 is cited. Operating cost is built bottom-up from duty, never as a percentage of capital; gravity sewers are priced by diameter and depth band; every option, including a costed do-nothing baseline, carries its own pumping, storage and energy | Project doctrine, 1 September 2026, on G1-p57 §7.1 and p95 to 96 |
| Value engineering | A formal study by an independent certified consultant at concept and preliminary stages for projects of OMR 5 million or more; the footnote lowers the trigger to any treatment plant or pumping station over OMR 2 million | G1-p93 §11.2 Table 27 |
| Cost and schedule accuracy | Feasibility ±30 %; preliminary and concept ±20 %; detailed ±10 %. A flood protection assessment at all three phases | G1-p17 to 20 §1.6 Table 2 |
| Remote areas | About 25 km or more from a centralised network, or under 500 residents or 100 plots at the end of the design period: septic tanks to the Oman Private Sewage Disposal Code, holding tanks emptied by vacuum tanker, or package plants for 50 to 5,000 inhabitants with at least one day of effluent storage | G1-p80 §8.1; p83 to 84 §8.4 |

# 19  Surveys and investigations

Table 25   Survey criteria (G203 §13, pages 197 to 199; G1 §5)

| Item | Requirement or value | Reference |
| --- | --- | --- |
| Topographic survey | Along the proposed routes with X, Y and Z on the Omani national datum in metric units; existing utilities and adjacent roads with cross-sections near the pipelines; grid, permanent benchmark and invert levels of existing drains on the maps; the designer selects the terrain model | G203-p197 |
| Accuracy by stage | At 95 % confidence: feasibility 1 to 5 m horizontal and 0.5 to 2 m vertical, an existing DEM acceptable; preliminary and concept 0.25 to 1.0 m horizontal and 0.05 to 0.5 m vertical, by UAV photogrammetry with ground control, LiDAR or GNSS RTK; detailed 0.02 to 0.10 m horizontal and 0.01 to 0.05 m vertical. The 0.5 m terrain blend used for design is checked against this at the survey | G1-p36 Table 5 |
| Control | Benchmarks to ±0.05 m, at least Order C Class 3 GPS | G203-p198 §13.3 |
| Underground services | Detection covering oil, gas, water and effluent pipelines, cables and irrigation falaj, by trial pits, probes between manholes, ground radar and electro-location | G203-p198 §13.3 |
| Existing assets | CCTV to NF EN 13508-2, a designer obligation to carry out and to provide with the tender documents; CCTV, topographic and geotechnical surveys at the early design stage | G203-p197 to 198 |
| Plant and station sites | Full plot dimensions, GPS coordinates of every boundary corner, surface strata, coverage extending 10 m beyond the plot limits | G203-p198 §13.2 |
| Geotechnical | Boreholes to 5.0 m below the pipe invert for shallow pipelines. Secondary and tertiary gravity sewers: a trial trench to 3.0 m or a borehole beyond, at 100 m spacing; primary sewers and force mains at 500 m. Geophysical investigation at the earliest stage for plants, stations and major wadi, falaj and road crossings | G203-p199 §13.4; G1-p40 to 41 Table 7 |

# 20  Register of project decisions and assumptions

Every value below is ours rather than the guideline's. A decision stands until the engineer changes it. An assumption is pending data and is replaced when the data arrives; each states what replaces it.

Table 26   Decisions and assumptions carried by the design

| Item | Value | Status | Basis and what replaces it |
| --- | --- | --- | --- |
| Maximum cover | 12.0 m, no exception, at chambers and along the trench | Decision, 7 September 2026 | The guideline's trigger is excavation cost; no costing exists at concept. Revisited per excursion when the cost analysis exists |
| Tractive tension | 1 Pa | Assumption, gap 9 | G203 gives no numeric value. Confirm with NWS; at 2 Pa a large share of DN200 pipes need a steeper gradient |
| Minimum tractive design flow | 1.5 L/s | Assumption | Mara's minimum design flow; without a floor the equation demands unbounded slopes as the flow tends to zero |
| PVC-U wall class | SDR34, SN8 | Assumption | Sets the true bore behind the hydraulics; the actual class per PAM-SPC-207 from NWS |
| Occupancy rate | 5.32 project basis; 5.0 in the W13 test-area run | Decision, 30 August 2026; open item for W13 | Measured from settlement population and counted domestic properties; recomputed when the clean plot layer lands. The test-area gate figures were produced at 5.0 and the full-area run is to apply 5.32 |
| Properties per plot | Counted; 1.0 fallback | Data, 19 August 2026 | Electricity accounts; the fallback applies only to a plot with no account |
| Wadi ground | Flood hazard classes 4, 5 and 6 of the 50-year grid | Assumption | Stands in for the guideline's washout criterion; settled by a scour-depth check |
| Reduced cover at a wadi crossing | Not available | Position | The guideline is silent; the 1.5 m answers scour and the encasement answers load |
| Lateral length cap | 45 m on riders and lateral sewers alike | Decision | The conservative reading of G203 Table 6 and §3.2 |
| Inlet angle | 85° applied; sharper than 75° flagged | Decision, 20 August 2026; deviation | Avoids about 200 bend chambers that served no construction purpose; see Section 21 |
| Gradient steps | 0.05 % | Decision, 23 August 2026 | The drawing value is the design value |
| Chamber spacing | 100 m split, rounded to 10 m, 5 m fallback | Decision, 18 August 2026 | Satisfies every spacing class of G203 Table 12 |
| Chamber separation | 3.0 m | Convention | No minimum exists in the guidelines |
| Chamber sizes | DN1000 to 3 m, DN1200 to 6 m, DN1500 deeper | Convention | The guideline says only sufficient size |
| Kerb clearances for gravity sewers | 1 m pipe, 0.5 m chamber | Inference | A force-main clause at G203-p51 applied to gravity |
| House drain outlet | 0.60 m below plot ground; 2 % blended fall | Method choice | Concept-stage connectability test only |
| Wall and bedding allowance | 0.05 m | Assumption | Below the crown cover in the invert-depth calculation |
| Infiltration order | Added unpeaked | Assumption | G1 does not state whether infiltration is peaked; confirm at kickoff |
| Peak factor below 100 properties | Held at the 100-property value | Method choice | The guideline prescribes no formula below 100 |
| G1 Table 12 drivers | Not applied | Decision, 30 August 2026 | Floor area, pupils, beds and employees are not supplied; adopt G1 Table 12 when real quantities arrive, never with the ratios |
| Road corridor thresholds | Collinear 10°, bend 30°, gate search 45 m, frontage 40 m | Method choices | Tuned on review |
| Dual carriageway rules | Excluded; crossings ≤ 70 m, within 25° of square, charged 2,500 m; underpass radius 30 m | Decision, 19 to 21 August 2026 | Section 9 |
| Join charge onto the main pipe | 400 m equivalent | Decision, 20 August 2026 | Fewer than 15 joins costs a pumping station on the test area |
| Pumping pockets | Under 50 plots absorbed | Rule | Detail design item |
| Cascading stations; rising-main duty rule | Not settled | Open, 7 September 2026 | Decided when the design raises them |

# 21  Deviations to be declared to NWS

Each item below departs from the letter of a guideline clause. Each is stated in the deliverable and NWS agreement is sought.

Table 27   Deviations and the agreement sought

| Deviation | Guideline clause | What the design does and why |
| --- | --- | --- |
| Inlet angle of 85° rather than 90° | G203-p30, "shall" | Enforcing 90° at every street junction inserted about 200 bend chambers a few metres short of junctions for no construction benefit. The design applies 85°, flags any inlet sharper than 75° for a purpose-made chamber with a curved channel, and never adds a chamber to satisfy the rule |
| Occupancy from electricity accounts | G1-p58 defines the rate as population ÷ NCSI housing units | Housing units are not published at settlement level, so counted domestic properties stand in for them. Validated by coverage within 2.0 points (Section 12.2) |
| Spatial allocation of non-domestic flow | G1-p59 §7.3.1 describes "spatially distributed non-domestic consumption" added to domestic consumption | The uplift is concentrated on the commercial and government plots rather than spread across the population. The total is preserved; a residential-only branch generates no commercial flow. Measured effect: project total unchanged, zone totals move between −17 % and +127 % |
| Planning-tier ratios in a project-specific design | G1-p60 §7.3.2 and p61 §7.3.3, "shall" use G1 Table 12 where detailed land use exists | The G1 Table 12 quantities have not been supplied, so the condition is unmet in substance. The 22 % and 14 % ratios set the volume as a labelled fallback and are replaced by G1 Table 12 when the data arrives |
| Weekly peak of 20 % in the Inception Report | G1 §7.4.2 gives Merrimack or Peltier only | The Inception Report applied a water-side peak-week concept on top of Peltier. The two peak twice; an NWS ruling is sought (Appendix A) |
| Infiltration at 10 % of flow in the Inception Report | G1-p72 §7.4.3 gives 720 L/day/km for new networks | The design applies 720 L/day/km per pipe; the Inception Report value is flagged for kickoff |
| Presence in a wadi where no other route exists | G203-p30 "must be avoided"; p33 "shall be avoided" | The design avoids it; where it cannot, the presence is a recorded and justified exception carried in the deliverable |

# Appendix A  Inception Report values against the guideline

The Inception Report Revision 0 and its demand workbook adopted the values below. Each is reconciled against the guideline clause; where the two differ the item is carried to Section 21.

Table 28   Inception Report R0 adoptions reconciled

| Item | Inception Report value | Against the guideline |
| --- | --- | --- |
| Population basis | NCSI wilayat series, Ibri 183,564 in 2024, growth about 2.4 to 3.0 % a year, settlement disaggregation | Consistent with G1-p58 |
| Domestic consumption, Adh Dhahirah | 163.5 L per head per day, computed from actual consumption 2021 to 2024 | Agrees with the 164 of G1 Table 11 |
| Return ratios | Domestic and tanker 0.85; non-domestic and governmental 0.54 | Equal to G1-p71 Table 19 |
| Infiltration | 10 % of wastewater flow, settlement-conditional | G1-p72 gives 720 L/day/km for new networks; flagged at kickoff |
| Tanker catchment | Settlements within 25 km of the plant | The 25 km is in G1-p80 §8.1, which defines a remote area as "approximately 25 km or more from existing centralized … networks" or under 500 residents or 100 plots at the end of the design period. The report reused it as a tanker-catchment radius; the reading is confirmed with NWS |
| Weekly peak | +20 % | Not in the G1 wastewater peaking chain. G1-p62 §7.3.6 defines a water-side peak day as "the average day consumption in the peak week (7-days rolling) excluding leakage"; the report appears to have carried it into the wastewater chain on top of Peltier. An NWS ruling is sought |
| Plant margin, effluent ratio, sludge | +10 %; treated effluent 95 % of inflow; sludge 0.25 kg/m³ | All three in G1-p73 and G1-p78 §7.4.7 |
| Treated effluent network loss | Not applied | G1-p76 requires a 10 % loss on produced effluent; the 95 % ratio alone overstates the deliverable volume by about 10 % |

G1-p59 §7.3 and G1-p70 §7.4: "In the absence of a developer-provided water demand calculation based on an approved methodology, the water demand shall be calculated in accordance with the methodology detailed below." G1-p60 Table 11: values "should be validated by NWS as essential design criteria, before designing the project".

Test-area result of the W13 pipeline on 7 September 2026, identical to the W8 design it was copied from. The built Nama network on the same ground also needs no pumping station.

G203-p27 §4.2.2.1. The equation is printed in the guideline as an image. Its simplified form without the tension term is valid only at τ = 1 Pa.

G203-p29 §4.3.1 Table 11.

Project decision of 7 September 2026. The limit binds nowhere on the test area, whose deepest cover is 10.45 m; it will bind when the design is extended to the whole study area, and that is where the cost question becomes real.

The built network in the test area, traced through its own manhole identifiers, is one trunk main, six sub mains and 419 laterals; 91 % of laterals drain into another lateral and only about sixteen pipes touch the trunk. The built network runs along a dual carriageway on 0.1 % of its length.

G1-p60 §7.3.2; G1-p61 §7.3.3; G1-p71 §7.4.1. Table 19 describes its own figures as "baseline figures [that] provide a general framework for planning and forecasting purposes across broader service areas" (G1-p70).

Ibri town alone measures 6.21. Five settlements are unusable pending boundary review: Sayh Al Masarrat, Al Jahli, Al Akheedar, Satwah and Al Qali. The figure is recomputed when the clean plot layer arrives.

G1-p59 §7.3.1: the ratios "do not apply to the water consumption of specific identified non-domestic projects such as economic zones". G1-p61 §7.3.4: special consumption "must be provided by the developer … These needs are not covered by population forecasts". G1-p70 §7.4 and §7.4.1: other water sources, binding. G1-p71 Table 19: tanker return rate.